Stride Academy (Athlos) Controls requirements

- Five (5) year warranty beginning after commissioning completion and punch list resolution

- All warranty work coordinated through EMS Administrator or Director of Facilities

- Software updates and firmware updates included perpetually (excludes labor)

- No Software Maintenance Agreements (SMAs) allowed

- All BAS software/hardware must operate perpetually without recurring licensing and SMAs

- Owner retains full rights to all project software and databases

- Owner receives ownership of graphics, programming code, databases, record drawings, and documentation

- Owner must have full security access for system operation, maintenance, and point generation

- Contractor must provide all software generation and programming tools

- Installer must be manufacturer authorized and trained

- Electrical components must comply with NFPA 70 requirements

- BAS system must comply with ASHRAE 135 BACnet standards

- Integrate all BAS points and programming per Owner standards

- BAS system must be Native BACnet

- System must support backward compatibility with legacy controllers of same brand

- Supervisory controllers cannot require point count or device licensing

- BACnet communications must use standard BACnet object types only

- Maintain consistent point addressing across equipment types

- Update all system software to latest version at project completion

Equipment Requirements

- HVAC equipment and RTUs shall be supplied as “controls ready” or “terminal strip” units

- Manufacturer supplied control packages are not permitted

- Manufacturer microprocessor controls using BACnet MS/TP are not acceptable as the primary RTU control medium

- All RTU controls shall be provided and installed by the Temperature Controls Contractor (TCC)

- Factory mounted dampers and actuators shall be provided by the equipment manufacturer

- Actuators shall operate on 24VAC power and accept 2-10VDC control signals from the TCC

  - Damper shall be controlled based on temperature, space CO2 and humidity

- VFDs and ECM motors shall be factory supplied and installed

- VFD and ECM control signals shall terminate at a low voltage terminal strip for TCC control

- Gas heat staging and modulation signals shall be brought to a low voltage terminal strip for TCC wiring and control

- Gas heating safeties and airflow interlocks shall remain factory hardwired mechanical/electrical safeties

- DX cooling staging and modulation signals shall be brought to a low voltage terminal strip for TCC wiring and control

- DX cooling safeties and interlocks shall remain factory hardwired mechanical/electrical safeties

- Controls contractor must maintain full visibility and control of equipment operation and programming

- Equipment operation including heating, cooling, and economizer functions shall be fully controlled by the TCC-provided BAS

- Equipment must provide ability for space dehumidification and shall include factory-installed hot gas reheat capability with all control points terminated to a low voltage terminal strip for full sequencing and control by the Temperature Controls Contractor (TCC)